## CENTRIFUGAL
PUMP CALCULATION PART 1
SYSTEM CHARACTERISTICS
| SINGLE STAGE CENTRIFUGAL PUMP CALCULATION | [12 empty] | Version | 1.001 | 1997-11-01 | Q | Ptot | Ltot | Ftot | Htot
| (Clean Water Use) | [15 empty] | 215 | 0 | -0.008 | 54.1284 | 54.1204
| Static Suction Lift = Ls |  |  |  | Pump Suction Diam = Ds
| Static Discharge Head = Ld |  |  |  | Pump Discharge Diam = Dd | [11 empty] | 0 | 0 | -0.008 | 0 | -0.008
| Total Static Head Ltot = Ls + Ld | [15 empty] | 26.875 | 0 | -0.008 | 0.84576 | 0.83776
| Friction Head = Hfs and Hfd | [15 empty] | 53.75 | 0 | -0.008 | 3.383 | 3.375
| Inlet and Discharge Nozzle Losses = Hi and Ho | [15 empty] | 80.625 | 0 | -0.008 | 7.6118 | 7.6038
| Velocity Head = V2/2g [often included in pump curves] | [15 empty] | 107.5 | 0 | -0.008 | 13.5321 | 13.5241
| Pump Suction and Discharge Nozzle Elevations = Lns and Lnd | [15 empty] | 134.375 | 0 | -0.008 | 21.1439 | 21.1359
| Suction Pressure Head = Ps [if open tank = 0] | [15 empty] | 161.25 | 0 | -0.008 | 30.4472 | 30.4392
| Discharge Pressure Head = Pd [if open tank = 0] | [15 empty] | 188.125 | 0 | -0.008 | 41.4421 | 41.4341
[17 empty] | 215 | 0 | -0.008 | 54.1284 | 54.1204
[17 empty] | 241.875 | 0 | -0.008 | 68.5063 | 68.4983
[17 empty] | 268.75 | 0 | -0.008 | 84.5757 | 84.5677
[17 empty] | 295.625 | 0 | -0.008 | 102.3366 | 102.3286
[17 empty] | 322.5 | 0 | -0.008 | 121.789 | 121.781
[7 empty] | Pout = Pd + Ld + Hfd + Ho - Lnd = Hd - Vd2/2g - Lnd | [9 empty] | 349.375 | 0 | -0.008 | 142.9329 | 142.9249
[17 empty] | 376.25 | 0 | -0.008 | 165.7683 | 165.7603
[17 empty] | 403.125 | 0 | -0.008 | 190.2953 | 190.2873
[6 empty] | Pin = Ps - Ls - Hfs - Hi + Lns = - Hs - Vs2/2g + Lns | [10 empty] | 430 | 0 | -0.008 | 216.5138 | 216.5058
[17 empty] | 215 |  |  |  | 55.5298
[5 empty] | Total Dynamic Suction Lift |  |  | Hs = Ls - Ps + Hfs + Hi - Vs2/2g |  |  |  | Dynamic Suction Lift (req'd) |  |  | Hs(r) = Ls - Ps + Hfs + Hi |  | WATER VAPOUR PRESSURE
[5 empty] | Total Dynamic Discharge Head |  |  | Hd = Ld + Pd + Hfd + Ho + Vd2/2g |  |  |  | Dynamic Discharge Head (req'd) |  |  | Hd(r) = Ld + Pd + Hfd + Ho |  | degC | kPa(abs)
[5 empty] | Total Dynamic Head |  |  | Htot = Hd + Hs |  |  |  | Dynamic Head (req'd) |  |  | Htot(r) = Hd(r) + Hs(r) |  | 0 | 0.6
[12 empty] | NPSHa(req'd) |  |  | NPSHa(r) = NPSHa - Vs2/2g |  | 15 | 1.7
|  | Closed Tank: | NPSHa(abs) = Ps + Patm - Ls - Hfs - Hi + Vs2/2g - Pvap [where Pvap = Vapour Pressure(abs)] | [8 empty] | Provide this to pump vendor and use on pump curves |  |  |  |  | 25 | 3.2
|  | Open Tank: | or = Pamb - Ls - Hfs - Hi + Vs2/2g - Pvap [NPSHa should exceed NPSHr by at least 0.5 m] | [8 empty] | where velocity head is included in vendors pump curves. |  |  |  |  | 30 | 4.25
[17 empty] | 40 | 7.38
| SYSTEM PROPERTIES | [5 empty] | SYSTEM CHARACTERISTICS | [5 empty] | PUMP SELECTION (Nominal) |  |  |  | 50 | 12.5
| Q | 215 | l/sec | 0.215 | m3/sec |  | Patm | 10.3287 | m | 101.325 | kPa(abs)
| SG | 1 | D | 1000 | kg/m3 |  | Pamb | 9.9796 | m | 97.9 | kPa(abs) |  | Pump Speed |  | 1483 | rpm | 120 | 198.5
| Tfluid |  |  | 16 | oC |  | Vs | 0.97777 | m | 4.3799 | m/sec | [5 empty] | 140 | 361.4
| Pvap | 0.19368 | m(abs) | 1.9 | kPa(abs) |  | Pinlet | -2.6687 | m | -26.1803 | kPa(g) |  | Impeller Diam |  | 0.449 | m
| Ps | 0 | m | 0 | kPa(g) |  | Hs | 1.991 | m | 19.5313 | kPa |  | Pump Head |  | 61.9546 | m
| Ls | 0.93 | m | 9.1233 | kPa |  | Hs(r) | 2.9687 | m | 29.1233 | kPa
| Hi | 0 | m | 0 | kPa |  | Vd | 2.3871 | m | 6.8437 | m/sec |  | Hydraulic Power |  | 117.1207 | kW | NOTES:
| Hfs | 2.0387 | m | 20 | kPa |  | Poutlet | 51.4517 | m | 504.7412 | kPa(g) |  | Pump Efficiency |  | 83.8% |  | For Hfs and Hfd try 50 kPa/100m
| Ds | 0.25 | m As | 0.049087 | m2 |  | Hd | 53.5388 | m | 525.2161 | kPa |  | Motor Power |  | 139.7622 | kW
| Lns | 0.3 | m | 2.943 | kPa |  | Hd(r) | 51.1517 | m | 501.7982 | kPa | [5 empty] | Select Ds and Dd for Vs and Vd around 3 m/sec
| Pd | 0 | m | 0 | kPa(g) | [7 empty] | Specific Speed |  | 1068.9706
| Ld | -0.938 | m | -9.2018 | kPa |  | Htot | 55.5298 | m | 544.7474 | kPa | [5 empty] | For small pumps try 60% efficiency
| Ho | 0 | m | 0 | kPa |  | Htot(r) | 54.1204 | m | 530.9215 | kPa |  | NPSHr |  | 2 | m
| Hfd | 52.0897 | m | 511 | kPa | [7 empty] | Normally approx. 3% Htot = |  | 1.6659 | m
| Dd | 0.2 | m Ad | 0.031416 | m2 |  | NPSHa | 7.795 | m(abs) | 76.4687 | kPa(g)
| Lnd | -0.3 | m | -2.943 | kPa |  | NPSHa(r) | 6.8172 | m(abs) | 66.8767 | kPa(g)